## Radiators (A)
Hydronic balancing in existing buildings
Determination of the volume flows for the static line balancing of heating systems with space heaters based on the heating load or the heat requirement or the heat output of the existing radiators and the temperature difference of the heating system.
A) | Determination of the heating load: The specific building heat load [W/m²] is determined by a heat load calculation according to DIN EN 12831 or an approximate calculation method. For a rough estimate of the heating load for existing buildings, the characteristic values from the adjacent table can be used. However, the application of these characteristic values does not replace an exact calculation of the heating load. | [16 empty] | Empirical values for the specific heat load of existing buildings to estimate the heat load
[18 empty] | Construction year |  | Specific heat load
B) | Determination of the space heating requirement or the radiator heat output: The heat demand per room is taken from an underlying heat demand calculation. If this data is not available, the existing radiators can be included with this form. With this data, the heat output of the radiator can be determined using manufacturer documents. | [16 empty] | Until 1970, uninsulated |  |  |  | 120…180 W/m²
[18 empty] | 1977 to 1984 |  |  |  | 70…100 W/m²
[18 empty] | 1985 to 1995 |  |  |  | 50…70 W/m²
[18 empty] | New building, EnEV |  |  |  | 40…50 W/m²
[18 empty] | New building, KfW 40/60 |  |  |  | 20…30 W/m²
| Application note: At the bottom of the screen, select the tab with the application you want. You can use the TAB key to navigate between the selection and input fields with a blue background. After selecting or entering, press the TAB key. | [16 empty] | Passive House |  |  |  | 10…15 W/m²
[18 empty] | Selection: |  | 60 |  | W/m²
Total room areas
1 |  |  | Manifold: |  | 69 |  |  | m² |  | Room size: | 21 | m² |  |  | Room size: | 21 | m² |  | Room size: | 16 | m² |  | Room size: | 11 | m² | Room size: | m² | Room size: | m² | Room size: | m²
[10 empty] | Length: |  | mm |  |  | Length: |  | mm |  | Length: |  | mm |  | Length: |  | mm | Length: | mm | Length: | mm | Length: | mm
[10 empty] | Height: |  | mm |  |  | Height: |  | mm |  | Height: |  | mm |  | Height: |  | mm | Height: | mm | Height: | mm | Height: | mm
[10 empty] | Depth: |  | mm |  |  | Depth: |  | mm |  | Depth: |  | mm |  | Depth: |  | mm | Depth: | mm | Depth: | mm | Depth: | mm
[10 empty] | Heat output: |  | W |  |  | Heat output: |  | W |  | Heat output: |  | W |  | Heat output: |  | W | Heat output: | W | Heat output: | W | Heat output: | W
[10 empty] | Radiator |  |  |  |  | Radiator |  |  |  | Radiator |  |  |  | Radiator |  |  | Radiator |  | Radiator |  | Radiator
Total room areas
1 |  |  | Manifold: |  | 84 |  |  | m² |  | Room size: | 21 | m² |  |  | Room size: | 21 | m² |  | Room size: | 21 | m² |  | Room size: | 21 | m² | Room size: | m² | Room size: | m² | Room size: | m²
[10 empty] | Length: |  | mm |  |  | Length: |  | mm |  | Length: |  | mm |  | Length: |  | mm | Length: | mm | Length: | mm | Length: | mm
[10 empty] | Height: |  | mm |  |  | Height: |  | mm |  | Height: |  | mm |  | Height: |  | mm | Height: | mm | Height: | mm | Height: | mm
[10 empty] | Depth: |  | mm |  |  | Depth: |  | mm |  | Depth: |  | mm |  | Depth: |  | mm | Depth: | mm | Depth: | mm | Depth: | mm
[10 empty] | Heat output: |  | W |  |  | Heat output: |  | W |  | Heat output: |  | W |  | Heat output: |  | W | Heat output: | W | Heat output: | W | Heat output: | W
[10 empty] | Radiator |  |  |  |  | Radiator |  |  |  | Radiator |  |  |  | Radiator |  |  | Radiator |  | Radiator |  | Radiator
|  | Flow temperature | [7 empty] | 80 | °C |  |  |  | 20 | K |  |  | Balancing valve selection
TacoSetter Bypass 100
[10 empty] | 60 | °C
|  | Return temperature | [12 empty] | Temperature difference |  |  |  | Dimension | Range |  | l/min
[19 empty] | DN 15 |  | 2-8 l/min | 6.5778
| Calculation of the volume flows for the balancing of the branches: | [17 empty] | DN 20 |  | 4-15 l/min | 6.5778
[19 empty] | DN 20 |  | 8-30 l/min | 6.5778
A) |  | Heating load Q [W] = specific heating load [W/m²] x sum of all room areas | [16 empty] | DN 25 |  | 6-20 l/min | 6.5778
[19 empty] | DN 25 |  | 10-40 l/min | 6.5778
|  |  | 60 |  |  |  | W/m² x |  |  | 153 |  | m² | = | 9180 |  | W |  |  | DN 32 |  | 20-70 l/min | 6.5778
[19 empty] | DN 40 |  | 30-120 l/min | 6.5778
B) |  | Heat load Q [W] = total heat output in line | [16 empty] | DN 50 |  | 50-200 l/min | 6.5778
TacoSetter Bypass Flange
Flow rate in the line:
|  | . |  |  |  | . | [12 empty] | Dimension | Range |  | l/min
|  | V | = |  |  | Q |  |  | = | 9180 |  | W |  | = | 6.5778 |  | l |  | DN 65 |  | 60-325 l/min | 6.5778
|  |  |  | c x (TVL-TRL) | [5 empty] | c x | 20 | K |  |  |  |  | min |  | DN 80 |  | 75-450 l/min | 6.5778
[19 empty] | DN 100 |  | 100-650 l/min | 6.5778
|  | c = | Constant for the specific heat capacity of water (1.163 Wh / l x K)
The formula contains the conversion of the unit [l/h] into [l/min]
Anzahl Stockwerke | [8 empty] | Heizlast
1 | [8 empty] | 10
2 | [8 empty] | 15
3 | [8 empty] | 20
4 | [8 empty] | 25
5 | [8 empty] | 30
6 | [8 empty] | 35
7 | [8 empty] | 40
8 | [8 empty] | 45
9 | [8 empty] | 50
10 | [8 empty] | 60
11 | [8 empty] | 70
12 | [8 empty] | 80
13 | [8 empty] | 90
14 | [8 empty] | 100
15 | [8 empty] | 110
16 | [8 empty] | 120
17 | [8 empty] | 130
18 | [8 empty] | 140
19 | [8 empty] | 150
20 | [8 empty] | 160
21 | [8 empty] | 170
22 | [8 empty] | 180
23 | [8 empty] | 190
24 | [8 empty] | 200
25 | [8 empty] | 210
26 | [8 empty] | 220
27 | [8 empty] | 230
28 | [8 empty] | 240
29 | [8 empty] | 250
30 | [8 empty] | 300

## Radiators (B)
Hydraulic balancing in existing buildings
Determination of the volume flows for the static line balancing of heating systems with space heaters based on the heating load or the heat requirement or the heat output of the existing radiators and the temperature difference of the heating system.
A) | Determination of the heating load: The specific building heat load [W/m²] is determined by a heat load calculation according to DIN EN 12831 or an approximate calculation method. For a rough estimate of the heating load for existing buildings, the characteristic values from the adjacent table can be used. However, the application of these characteristic values does not replace an exact calculation of the heating load.
B) | Determination of the space heating requirement or the radiator heat output: The heat demand per room is taken from an underlying heat demand calculation. If this data is not available, the existing radiators can be included with this form. With this data, the heat output of the radiator can be determined using manufacturer documents.
Application note: At the bottom of the screen, select the tab with the application you want. You can use the TAB key to navigate between the selection and input fields with a blue background. After selecting or entering, press the TAB key.
Total heat output
1 |  |  | Manifold: |  | 2950 |  | W
[9 empty] | 1200 |  |  |  |  | 900 |  |  | 800
[8 empty] | Length: |  | mm |  |  | Length: |  | mm | Length: |  | mm |  | Length: | mm | Length: | mm | Length: | mm | Length: | mm
[9 empty] | 500 |  |  |  |  | 500 |  |  | 600
[8 empty] | Height: |  | mm |  |  | Height: |  | mm | Height: |  | mm |  | Height: | mm | Height: | mm | Height: | mm | Height: | mm
[9 empty] | 115 |  |  |  |  | 115 |  |  | 115
[8 empty] | Depth: |  | mm |  |  | Depth: |  | mm | Depth: |  | mm |  | Depth: | mm | Depth: | mm | Depth: | mm | Depth: | mm
[9 empty] | 1250 |  |  |  |  | 850 |  |  | 850
[8 empty] | Heat output: |  | W |  |  | Heat output: |  | W | Heat output: |  | W |  | Heat output: | W | Heat output: | W | Heat output: | W | Heat output: | W
[8 empty] | Number of radiators: |  | 1 |  |  | Number of radiators: |  | 1 | Number of radiators: |  | 1 |  | Number of radiators: | 1 | Number of radiators: | 1 | Number of radiators: | 1 | Number of radiators: | 1
Total heat output
1 |  |  | Manifold: |  | 2700 |  | W
[9 empty] | 1200 |  |  |  |  | 900 |  |  | 1400
[8 empty] | Length: |  | mm |  |  | Length: |  | mm | Length: |  | mm |  | Length: | mm | Length: | mm | Length: | mm | Length: | mm
[9 empty] | 500 |  |  |  |  | 500 |  |  | 600
[8 empty] | Height: |  | mm |  |  | Height: |  | mm | Height: |  | mm |  | Height: | mm | Height: | mm | Height: | mm | Height: | mm
[9 empty] | 115 |  |  |  |  | 115 |  |  | 115
[8 empty] | Depth: |  | mm |  |  | Depth: |  | mm | Depth: |  | mm |  | Depth: | mm | Depth: | mm | Depth: | mm | Depth: | mm
[9 empty] | 1250 |  |  |  |  | 850 |  |  | 600
[8 empty] | Heat output: |  | W |  |  | Heat output: |  | W | Heat output: |  | W |  | Heat output: | W | Heat output: | W | Heat output: | W | Heat output: | W
[8 empty] | Number of radiators: |  | 1 |  |  | Number of radiators: |  | 1 | Number of radiators: |  | 1 |  | Number of radiators: | 1 | Number of radiators: | 1 | Number of radiators: | 1 | Number of radiators: | 1
[9 empty] | 70 | °C | Temperature difference Flow temperature |  |  | 20 | K | Balancing valve selection
Total heat output
TacoSetter Bypass 100
|  |  | Line: |  | 5650 |  | W |  | 50 | °C | Return temperature
[16 empty] | Dimension | Range |  | l/min
[16 empty] | DN 15 |  | 2-8 l/min | 4.0484
| Calculation of the volume flows for the branch balancing: | [14 empty] | DN 20 |  | 4-15 l/min | 4.0484
[16 empty] | DN 20 |  | 8-30 l/min | 4.0484
A) |  | Heating load Q [W] = specific heating load [W/m²] x sum of all room areas | [13 empty] | DN 25 |  | 6-20 l/min | 4.0484
[16 empty] | DN 25 |  | 10-40 l/min | 4.0484
[16 empty] | DN 32 |  | 20-70 l/min | 4.0484
B) |  | Heat load Q [W] = total heat output in line | [13 empty] | DN 40 |  | 30-120 l/min | 4.0484
[16 empty] | DN 50 |  | 50-200 l/min | 4.0484
|  | Flow rate in the line: | [13 empty] | TacoSetter Bypass Flange
|  | . |  |  |  | .
|  | V | = |  |  | Q | = | 5650 |  | W |  | = | 4.0484 |  | l | Dimension | Range |  | l/min
|  |  |  | c x (TVL-TRL) |  |  |  | c x | 20 | K |  |  |  |  | min | DN 65 |  | 60-325 l/min | 4.0484
[16 empty] | DN 80 |  | 75-450 l/min | 4.0484
[16 empty] | DN 100 |  | 100-650 l/min | 4.0484
|  | c = | Constant for the specific heat capacity of water (1.163 Wh / l x K)
The formula contains the conversion of the unit [l/h] into [l/min]
Anzahl Stockwerke
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30

## Underfloor heating (A)
Hydronic balancing in existing buildings
| Determination of the volume flows for the static line balancing of heating systems with space heaters based on the heating load or the heat requirement or the heat output of the existing radiators and the temperature difference of the heating system. | [14 empty] | Drücken Sie nach Auswahl oder Eingabe jeweils die TAB-Taste.
A) | Determination of the heating load: The specific building heat load [W/m²] is determined by a heat load calculation according to DIN EN 12831 or an approximate calculation method. For a rough estimate of the heating load for existing buildings, the characteristic values from the adjacent table can be used. However, the application of these characteristic values does not replace an exact calculation of the heating load. | [14 empty] | Empirical values for the specific heat load of existing buildings to estimate the heat load
[16 empty] | Construction year |  | Specific heat load
B) | Determination of the space heating requirement or the radiator heat output: The heat demand per room is taken from an underlying heat demand calculation. If this data is not available, the existing radiators can be included with this form. With this data, the heat output of the radiator can be determined using manufacturer documents. | [14 empty] | Until 1970, uninsulated |  |  |  | 120…180 W/m²
[16 empty] | 1977 to 1984 |  |  |  | 70…100 W/m²
[16 empty] | 1985 to 1995 |  |  |  | 50…70 W/m²
[16 empty] | New building, EnEV |  |  |  | 40…50 W/m²
[16 empty] | New building, KfW 40/60 |  |  |  | 20…30 W/m²
| Application note: At the bottom of the screen, select the tab with the application you want. You can use the TAB key to navigate between the selection and input fields with a blue background. After selecting or entering, press the TAB key. | [14 empty] | Passive House |  |  |  | 10…15 W/m²
Correction factors for heat transfer values of different floor coverings
[18 empty] | Tiling: | fB = | 1
[18 empty] | Laminate floor: | fB = | 1.2
[18 empty] | Carpet, parquet floor: | fB = | 1.3
[16 empty] | Selection: |  | 60 |  | W/m²
Total heat output
|  |  | Manifold: |  | 2880 |  | W
1 | [7 empty] | Room size: | 16 | m² |  |  | Room size: | 11 | m² |  | Room size: | 21 | m² |  |  | Room size: |  | m² |  | Room size: |  | m² |  | Room size: |  | m² |  | Room size: |  | m²
[8 empty] | Correction factor: | 1 |  |  |  | Correction factor: | 1 |  |  | Correction factor: | 1 |  |  |  | Correction factor: |  |  |  | Correction factor: |  |  |  | Correction factor: |  |  |  | Correction factor:
[8 empty] | Flow rate: | 1.9654 | l/min |  |  | Flow rate: | 1.3512 | l/min |  | Flow rate: | 2.5795 | l/min |  |  | Flow rate: | 0 | l/min |  | Flow rate: | 0 | l/min |  | Flow rate: | 0 | l/min |  | Flow rate: | 0 | l/min
[7 empty] | Number of heating circuits: |  |  | 1 |  | Number of heating circuits: |  |  | 1 | Number of heating circuits: |  |  | 1 |  | Number of heating circuits: |  |  | 1 | Number of heating circuits: |  |  | 1 | Number of heating circuits: |  |  | 1 | Number of heating circuits: |  |  | 1
Total heat output
|  |  | Manifold: |  | 2220 |  | W
1 | [7 empty] | Room size: | 9 | m² |  |  | Room size: | 14 | m² |  | Room size: | 7 | m² |  |  | Room size: | 7 | m² |  | Room size: |  | m² |  | Room size: |  | m² |  | Room size: |  | m²
[8 empty] | Correction factor: | 1 |  |  |  | Correction factor: | 1 |  |  | Correction factor: | 1 |  |  |  | Correction factor: | 1 |  |  | Correction factor: |  |  |  | Correction factor: |  |  |  | Correction factor:
[8 empty] | Flow rate: | 1.1055 | l/min |  |  | Flow rate: | 1.7197 | l/min |  | Flow rate: | 0.85985 | l/min |  |  | Flow rate: | 0.85985 | l/min |  | Flow rate: | 0 | l/min |  | Flow rate: | 0 | l/min |  | Flow rate: | 0 | l/min
[7 empty] | Number of heating circuits: |  |  | 1 |  | Number of heating circuits: |  |  | 1 | Number of heating circuits: |  |  | 1 |  | Number of heating circuits: |  |  | 1 | Number of heating circuits: |  |  | 1 | Number of heating circuits: |  |  | 1 | Number of heating circuits: |  |  | 1
[9 empty] | 35 | °C | Temp. difference DT Flow temperature |  |  | 7 | K |  | Balancing valve selection
Total heat output
TacoSetter Bypass 100
|  |  | Line: |  | 5100 |  | W |  | 28 | °C | Return temperature
[17 empty] | Dimension | Range |  | l/min
[17 empty] | DN 15 |  | 2-8 l/min | 10.441
[17 empty] | DN 20 |  | 4-15 l/min | 10.441
| Calculation of the volume flows for the hydronic balancing: | [15 empty] | DN 20 |  | 8-30 l/min | 10.441
[17 empty] | DN 25 |  | 6-20 l/min | 10.441
[17 empty] | DN 25 |  | 10-40 l/min | 10.441
[17 empty] | DN 32 |  | 20-70 l/min | 10.441
A) |  | Flow rate in the line: | [14 empty] | DN 40 |  | 30-120 l/min | 10.441
|  | . |  |  |  | . | [10 empty] | DN 50 |  | 50-200 l/min | 10.441
|  | V | = |  |  | Q | = | 5100 |  | W |  | = | 10.441 |  | l |  | TacoSetter Bypass Flange
|  |  |  | c x (TVL-TRL) |  |  |  | c x | 7 | K |  |  |  |  | min
[17 empty] | Dimension | Range |  | l/min
|  | c = | Constant for the specific heat capacity of water (1.163 Wh / l x K) | [13 empty] | DN 65 |  | 60-325 l/min | 10.441
|  |  | The formula contains the conversion of the unit [l/h] into [l/min] | [13 empty] | DN 80 |  | 75-450 l/min | 10.441
[17 empty] | DN 100 |  | 100-650 l/min | 10.441
Anzahl Stockwerke | [6 empty] | Heizlast
1 | [6 empty] | 10
2 | [6 empty] | 15
3 | [6 empty] | 20
4 | [6 empty] | 25
5 | [6 empty] | 30
6 | [6 empty] | 35
7 | [6 empty] | 40
8 | [6 empty] | 45
9 | [6 empty] | 50
10 | [6 empty] | 60
11 | [6 empty] | 70
12 | [6 empty] | 80
13 | [6 empty] | 90
14 | [6 empty] | 100
15 | [6 empty] | 110
16 | [6 empty] | 120
17 | [6 empty] | 130
18 | [6 empty] | 140
19 | [6 empty] | 150
20 | [6 empty] | 160
21 | [6 empty] | 170
22 | [6 empty] | 180
23 | [6 empty] | 190
24 | [6 empty] | 200
25 | [6 empty] | 210
26 | [6 empty] | 220
27 | [6 empty] | 230
28 | [6 empty] | 240
29 | [6 empty] | 250
30 | [6 empty] | 300

## Underfloor heating (B)
Hydraulic balancing in existing buildings
Determination of the volume flows for the static line balancing of heating systems with space heaters based on the heating load or the heat requirement or the heat output of the existing radiators and the temperature difference of the heating system.
A) | Determination of the heating load: The specific building heat load [W/m²] is determined by a heat load calculation according to DIN EN 12831 or an approximate calculation method. For a rough estimate of the heating load for existing buildings, the characteristic values from the adjacent table can be used. However, the application of these characteristic values does not replace an exact calculation of the heating load.
B) | Determination of the space heating requirement or the radiator heat output: The heat demand per room is taken from an underlying heat demand calculation. If this data is not available, the existing radiators can be included with this form. With this data, the heat output of the radiator can be determined using manufacturer documents. | [14 empty] | Correction factors for heat transfer values of different floor coverings
[16 empty] | Tiling: |  |  | fB = | 1
[16 empty] | Laminate floor: |  |  | fB = | 1.2
| Application note: At the bottom of the screen, select the tab with the application you want. You can use the TAB key to navigate between the selection and input fields with a blue background. After selecting or entering, press the TAB key. | [14 empty] | Carpet, parquet floor: |  |  | fB = | 1.3
Total heat output
|  |  | Manifold |  | 2880 |  | W
1 | [7 empty] | Heat output: | 660 | W |  |  | Heat output: | 960 | W |  | Heat output: | 1260 | W |  |  | Heat output: |  | W |  | Heat output: |  | W |  | Heat output: |  | W |  | Heat output: |  | W
[8 empty] | Correction factor fB: | 1 |  |  |  | Correction factor fB: | 1 |  |  | Correction factor fB: | 1 |  |  |  | Correction factor fB: |  |  |  | Correction factor fB: |  |  |  | Correction factor fB: |  |  |  | Correction factor fB:
[8 empty] | Flow rate: | 1.3512 | l/min |  |  | Flow rate: | 1.9654 | l/min |  | Flow rate: | 2.5795 | l/min |  |  | Flow rate: | 0 | l/min |  | Flow rate: | 0 | l/min |  | Flow rate: | 0 | l/min |  | Flow rate: | 0 | l/min
[7 empty] | Number of heating circuits: |  |  | 1 |  | Number of heating circuits: |  |  | 1 | Number of heating circuits: |  |  | 1 |  | Number of heating circuits: |  |  | 1 | Number of heating circuits: |  |  | 1 | Number of heating circuits: |  |  | 1 | Number of heating circuits: |  |  | 1
Total heat output
|  |  | Manifold |  | 4050 |  | W
1 | [7 empty] | Heat output: | 1950 | W |  |  | Heat output: | 1200 | W |  | Heat output: | 900 | W |  |  | Heat output: |  | W |  | Heat output: |  | W |  | Heat output: |  | W |  | Heat output: |  | W
[8 empty] | Correction factor fB: | 1 |  |  |  | Correction factor fB: | 1 |  |  | Correction factor fB: | 1 |  |  |  | Correction factor fB: |  |  |  | Correction factor fB: |  |  |  | Correction factor fB: |  |  |  | Correction factor fB:
[8 empty] | Flow rate: | 3.9921 | l/min |  |  | Flow rate: | 2.4567 | l/min |  | Flow rate: | 1.8425 | l/min |  |  | Flow rate: | 0 | l/min |  | Flow rate: | 0 | l/min |  | Flow rate: | 0 | l/min |  | Flow rate: | 0 | l/min
[7 empty] | Number of heating circuits: |  |  | 1 |  | Number of heating circuits: |  |  | 1 | Number of heating circuits: |  |  | 1 |  | Number of heating circuits: |  |  | 1 | Number of heating circuits: |  |  | 1 | Number of heating circuits: |  |  | 1 | Number of heating circuits: |  |  | 1
[9 empty] | 35 | °C | Temp. difference DT Flow temperature |  |  | 7 | K |  | Balancing valve selection
Total heat output
TacoSetter Bypass 100
|  |  | Line: |  | 6930 |  | W |  | 28 | °C | Return temperature
[17 empty] | Dimension | Range |  | l/min
[17 empty] | DN 15 |  | 2-8 l/min | 14.1874
[17 empty] | DN 20 |  | 4-15 l/min | 14.1874
| Calculation of the volume flows for the hydronic balancing: | [15 empty] | DN 20 |  | 8-30 l/min | 14.1874
[17 empty] | DN 25 |  | 6-20 l/min | 14.1874
[17 empty] | DN 25 |  | 10-40 l/min | 14.1874
[17 empty] | DN 32 |  | 20-70 l/min | 14.1874
A) |  | Flow rate in the line: | [14 empty] | DN 40 |  | 30-120 l/min | 14.1874
|  | . |  |  |  | . | [10 empty] | DN 50 |  | 50-200 l/min | 14.1874
|  | V | = |  |  | Q | = | 6930 |  | W |  | = | 14.1874 |  | l |  | TacoSetter Bypass Flange
|  |  |  | c x (TVL-TRL) |  |  |  | c x | 7 | K |  |  |  |  | min
[17 empty] | Dimension | Range |  | l/min
|  | c = | Constant for the specific heat capacity of water (1.163 Wh / l x K) | [13 empty] | DN 65 |  | 60-325 l/min | 14.1874
|  |  | The formula contains the conversion of the unit [l/h] into [l/min] | [13 empty] | DN 80 |  | 75-450 l/min | 14.1874
[17 empty] | DN 100 |  | 100-650 l/min | 14.1874
Anzahl Stockwerke | [6 empty] | Heizlast
1 | [6 empty] | 10
2 | [6 empty] | 15
3 | [6 empty] | 20
4 | [6 empty] | 25
5 | [6 empty] | 30
6 | [6 empty] | 35
7 | [6 empty] | 40
8 | [6 empty] | 45
9 | [6 empty] | 50
10 | [6 empty] | 60
11 | [6 empty] | 70
12 | [6 empty] | 80
13 | [6 empty] | 90
14 | [6 empty] | 100
15 | [6 empty] | 110
16 | [6 empty] | 120
17 | [6 empty] | 130
18 | [6 empty] | 140
19 | [6 empty] | 150
20 | [6 empty] | 160
21 | [6 empty] | 170
22 | [6 empty] | 180
23 | [6 empty] | 190
24 | [6 empty] | 200
25 | [6 empty] | 210
26 | [6 empty] | 220
27 | [6 empty] | 230
28 | [6 empty] | 240
29 | [6 empty] | 250
30 | [6 empty] | 300